Header Text	Comment	DB Node
		1	2	3	4
Some Text
The Oracle Exadata Database Machine can have 2 different types of database server: / X9M-2 with 2 to 19 Oracle Server X9M-2 database servers, / X9M-8 with 2 or 3 Oracle Server X9M-8 database servers. / Refer to the Assumptions on page Error: Reference source not found for requirements/suggestions for using laptops for this work. / When connecting to the ILOM Serial Management port on the Database Nodes the baud rate setting on the servers could be either 115200,8,N,1 or 9600,8,N,1 / For customers planning to use OVS, do most of the checklist below as Linux and then convert the DB nodes to KVM later by ACS. / The first DB node will be in RU 16 working upwards. For “Base Config” racks only DB Nodes 1 & 2 are present (this section of the checklist is laid out for up to 4 DB nodes). For additional DB Nodes use the additional “swim-lanes” on page Error: Reference source not found of this checklist. / If any of the profile checks fail and any firmware needs to be reflashed, then contact the Exadata Enterprise Support Team (EEST) to open a collaboration SR to RHS x86 task from the Install SR. Follow the process described on page Error: Reference source not found of this checklist.
Power on all servers in the rack (Power button on front panel). Each server will boot itself up through BIOS and boot the OS with the IP configuration. / The X9M-8 servers may take between 60 & 70 minutes to boot through the normal BIOS POST tests. During this time the BIOS POST progress will appear on the ILOM graphical console but not on the serial console. / After the first initial boot the Exadata image will reboot again, taking another 15+ minutes before starting and completing the elastic configuration setup to the login prompt.
DB01 only: / Either connect a serial cable between the server’s serial MGT port and a laptop or similar device OR use a laptop connected to the Cisco switch on 192.168.1.x to SSH to the DB01 ILOM. / Then connect to the console & login to the host.	Do NOT use port 48 on the Cisco for a laptop – use any other free port or temporarily one of the PDU ports. / -> start /SP/console <Press Return key> node16.domain.mycompany.com login: user=root pwd=welcome1 / If DB01 is an X9M-8 server, the initial hostname will also be node16 (refer to table on page Error: Reference source not found and description on page Error: Reference source not found).
All other DB servers: / Login via SSH from the DB01 OS connection to the server's IP address (using the tables on pages Error: Reference source not found and Error: Reference source not found).	Example: ru17.domain.mycompany.com login: user=root password=welcome1 / If DB02 is an X9M-8 server, the initial hostname will be ru24.
Verify the baud rate for the serial console ports are set correctly by manufacturing, should be set to 115200,8,N,1 / -> show -l all /SP/serial/ / …. <snip> / /SP/serial/external / Properties: / commitpending = (Cannot show property) / flowcontrol = none / pendingspeed = 9600 / speed = 9600 / /SP/serial/host / Properties: / autobaud = disabled (Host: 115200 bps, Console-TTY: 115200 bps) / commitpending = (Cannot show property) / flowcontrol = none / pendingautobaud = disabled / pendingflowcontrol = none / pendingspeed = 115200 / speed = 115200 / Correct the pending speed if incorrect: / -> set /SP/serial/external pendingspeed=115200 / -> set /SP/serial/external =true

4

Task	Comments	Check

Check